1999 REPAIR HISTORY FOR DDG 58 USS LABOON

SMARTSHIP SHIPBOARD SIMULATION SYSTEMS

Ann Christine Catlin

August 29, 2005

This report investigates the repair history for the USS Laboon extracted from the 1999 Ships 3M Database for Electrical Power Generation/Distribution Systems and Propulsion Systems. The information will assist in identifying

- The precise configuration, nomenclature and EICs of the electrical power generation, electrical power distribution systems and propulsion systems onboard a DDG class ship.

There was some guesswork involved in my attempt to map the shipboard equipment described by Vishal to the 3M EIC (due to the lack of SME guidance.) For those EICs appearing here, we are assured of the EIC and nomenclature accuracy.

- The failures and repairs of the electric power generation/distribution and propulsion systems that ACTUALLY took place over a one year period onboard a ship from the DDG class.

- The repairs with the longest ship’s force repair time in man-hours [top 20] for this data.

Other information can also be extracted from the original data, for example,

- the ‘top 20’ most frequent failures & repairs,

- the ‘top 20’ longest failure & repair down times,

- etc.

Hopefully when I speak with the SMEs, I can get information about repairs that affect the wireless/wired network the most. Ask if you want more analysis.

The following Ships 3M classifications are included in this report:

Section 1. 3xxxxxx: Electrical Power Generation Systems

DDG Equipment configuration in repair record         …. 	Page 3

Top 20 Longest Ship’s Force Repair Times     ………… 	Page 3

Complete listing of all repairs in 1999 …………………..	Page 3

Section 2. 4xxxxxx: Electrical Power Distribution Systems

DDG Equipment configuration in repair record         …. 	Page 8

Top 20 Longest Ship’s Force Repair Times     ………… 	Page 8

Complete listing of all repairs in 1999 …………………..	Page 8

Section 3. 5xxxxxx: Missile Systems

DDG Equipment configuration in repair record         …. 	Page 12

Top 20 Longest Ship’s Force Repair Times     ………… 	Page 12

Complete listing of all repairs in 1999 …………………..	Page 12

Section 4. 5xxxxxx:  Propulsion Systems

DDG Equipment configuration in repair record         …. 	Page 13

Top 32 Longest Ship’s Force Repair Times     ………… 	Page 13

Complete listing of all repairs in 1999 …………………..	Page 14

There are additional interesting classifications. Ask if you want more information about these.

Section 1. 3xxxxxx codes: Electrical Power Generation Systems repairs for the year 1999

3xxxxxx Equipment Configuration appearing in 3M repairs for this DDG class ship:

3500000		GENERATOR SET, GAS TURBINE

3510000		TURBINE ASSEMBLY, GAS, SSPU (GARRETT ME831)

3511000 	GAS TURBINE

3530000 	ENCLOSURE ASSEMBLY, BASE

3550000 	GENERATOR, AC

3561000		CONTROLS & INSTRUMENTS, ELECTRICAL, SSPU

3573000		SEPARATION SYSTEM, MOISTURE

3574000		AIR SYSTEM, COOLING

3576000		ANTI-ICING SYSTEM

3602000		CHARGERS, BATTERY

3705000		L.O. FILL AND TRANSFER, SHIPS'S SERVICE DIESEL GENERATOR

Longest repair man-hours for single repair for this ship (top 20)

| EIC | equipment_nomenclature | csmp_narrative_summary | man_hours | total_part_issues |
| --- | --- | --- | --- | --- |
| 3510000 | LOCAL CONTROL PA | 3GTG LOCAL FUEL TEMP CARD FAUL | 610 | 1 |
| 3511000 | ENGINE ASSY GAS | FAULTY LUBE OIL PRESSURE READ | 550 | 0 |
| 3576000 | EXCITATION CONTR | NR1 GTG LOSS OF OUTPUT VOLTAGE | 400 | 0 |
| 3511000 | ENGINE ASSY GAS | TURBINE TEMPS HIGH 2 GTG | 333 | 3 |
| 3511000 | ENGINE ASSY GAS | REPLACE 3GTG LIGHTHOUS SEALE | 260 | 14 |
| 3511000 | GOVERNOR, ELECTR | #3 GTG WILL NOT ADJUST FREQ | 210 | 0 |
| 3510000 | FILTER FDPRESS | REPLACE LUBE OIL FILTER | 120 | 3 |
| 3510000 | GENERATOR SET | MORMON CLAMP FAILED | 106 | 0 |
| 3511000 | ENGINE ASSY GAS | THERMOCOUPLE TEMPS HIGH | 101 | 0 |
| 3510000 | VALVE,CONTROL-TE | 2GTG TEMP REG VALVE FAILED | 90 | 1 |
| 3510000 | NOZZLE, FUEL ASS | CLOGGED F/O NOZZLES | 75 | 6 |
| 3602000 | BATTERY CHARGING | OVERHAUL STBD BOAT LCKR CHRGR | 62 | 2 |
| 3510000 | FILTER, DUAL | 2 GTG F/O FILTER CLOGGED | 60 | 2 |
| 3510000 | NOZZLE, FUEL ASS | FAILING FUEL NOZZLES #2 GTG | 60 | 6 |
| 3576000 | DAMPER, AIR COOL | VENT DAMPER FAILED TO CLOSE | 59 | 2 |
| 3510000 | FILTER, DUPLEX, | 2GTG CLOGGED L/O FILTERS | 55 | 1 |
| 3510000 | FILTER FDPRESS L | 2 GTG CLOGGED F/O FILTERS | 50 | 6 |
| 3550000 | GENERATOR A23938 | 3 GTG ZINC ANNODES ERODED | 50 | 2 |
| 3550000 | GENERATOR A23938 | 2 GTG ZINCS ERODED AWAY | 50 | 1 |
| 3510000 | MOTOR AC | TEST/REPAIR GTG AUX PUMP MOTOR | 44 | 0 |

Full listing of 3xxxxxx repairs for columns EIC, nomenclature, sailor narrative maintenance action summary, ship’s force man-hours and total part issues.

| EIC | equipment_nomenclature | csmp_narrative_summary | man_hours | total_part_issues |
| --- | --- | --- | --- | --- |
| 3510000 | NOZZLE, FUEL ASS | DIRTY NOZZLES | 20 | 1 |
| 3510000 | NOZZLE, FUEL ASS | DIRTY NOZZLE | 20 | 1 |
| 3510000 | NOZZLE, FUEL ASS | DIRTY NOZZLES | 20 | 2 |
| 3510000 | NOZZLE, FUEL ASS | DIRTY NOZZLES | 20 | 1 |
| 3510000 | FILTER FDPRESS L | LP F/O FILTER CLOGGED (GTM) | 5 | 3 |
| 3510000 | FILTER FDPRESS L | 1 GTG F/O FILTER CLOGGED | 7 | 7 |
| 3510000 | NOZZLE, FUEL ASS | FAULTY NOZZLES | 15 | 1 |
| 3510000 | NOZZLE, FUEL ASS | FAULTY FUEL NOZZLES | 15 | 1 |
| 3510000 | NOZZLE, FUEL ASS | FAULTY FUEL NOZZLES | 15 | 1 |
| 3510000 | NOZZLE, FUEL ASS | FAULTY NOZZLES | 15 | 1 |
| 3510000 | NOZZLE, FUEL ASS | FAULTY NOZZLES | 15 | 1 |
| 3510000 | NOZZLE, FUEL ASS | FAULTY FUEL NOZZLE | 15 | 1 |
| 3510000 | NOZZLE, FUEL ASS | NR 2 GTG HIGH TEMPS THERMOCOUP | 1 | 0 |
| 3510000 | LOCAL CONTROL PA | NUMEROUS BURNED LIGHT BULBS | 1 | 1 |
| 3510000 | NOZZLE, FUEL ASS | FAULTY FUEL NOZZLES HIGH TEMPS | 15 | 1 |
| 3510000 | NOZZLE, FUEL ASS | FAULTY FUEL NOZZLES HIGH TEMPS | 15 | 1 |
| 3510000 | NOZZLE, FUEL ASS | FAULTY FUEL NOZZLES HIGH TEMPS | 15 | 1 |
| 3510000 | NOZZLE, FUEL ASS | FAULTY FUEL NOZZLES HIGH TEMPS | 15 | 1 |
| 3510000 | NOZZLE, FUEL ASS | FAULTY FUEL NOZZLES HIGH TEMPS | 15 | 1 |
| 3510000 | NOZZLE, FUEL ASS | FAULTY FUEL NOZZLES HIGH TEMPS | 15 | 1 |
| 3510000 | FILTER, DUPLEX, | NR3 SSGTG L/O DUPLEX FILTERS | 1 | 1 |
| 3510000 | FILTER, DUAL | NR 2 SSGTG FO FILTERS | 4 | 1 |
| 3510000 | FILTER FDPRESS L | REPLACE F/O FILTER AND O-RING | 7 | 2 |
| 3510000 | FILTER, DUPLEX, | REPLACE ENG L/O FILTER | 7 | 2 |
| 3510000 | LOCAL CONTROL PA | 2 LOCOP DAMAGED PWR SUPPLY | 12 | 1 |
| 3510000 | FILTER, DUPLEX, | 3 SSGTG L/O FILTER SHIFT LEVER | 2 | 0 |
| 3510000 | VALVE, SOLENOID | F/O SHUT OFF VLV FOR POM | 1 | 0 |
| 3510000 | FILTER FDPRESS H | REPLACE HP FUEL FILTER | 6 | 3 |
| 3510000 | LOCAL CONTROL PA | BURNED OUT LIGHTS AT LOCOP | 2 | 1 |
| 3510000 | NOZZLE, FUEL ASS | REPLACE FUEL NOZZLES | 8 | 6 |
| 3510000 | FILTER FDPRESS | REPLACE LUBE OIL FILTER | 120 | 3 |
| 3510000 | NOZZLE, FUEL ASS | F/O NOZZLES FAILED | 36 | 7 |
| 3510000 | GENERATOR SET | MORMON CLAMP FAILED | 106 | 0 |
| 3510000 | LOCAL CONTROL PA | #1 GTG WATER WASH SWITCH FAULT | 4 | 1 |
| 3510000 | FILTER FDPRESS L | CHANGE F/O FILTER ELEMENTS | 16 | 6 |
| 3510000 | FILTER, DUPLEX, | NR#3 SSGTG L/O FILTERS CHG OUT | 4 | 2 |
| 3510000 | PUMP, MAIN PRESS | 3 GTG LOW L/O PRESSURE | 11 | 0 |
| 3510000 | FILTER, LUBE OIL | REPLACE L/O FILTER | 12 | 0 |
| 3510000 | LOCAL CONTROL PA | #3 GTG LIGHT BULBS OOC | 3 | 3 |
| 3510000 | FILTER FDPRESS L | REPLACE NR2 GTG F/O FILTERS | 3 | 3 |
| 3510000 | FILTER FDPRESS L | FILTERS ARE DIRTY | 8 | 8 |
| 3510000 | FILTER FDPRESS H | CHANGE OUT FILTERS | 14 | 4 |
| 3510000 | MOTOR AC | TEST/REPAIR GTG AUX PUMP MOTOR | 44 | 0 |
| 3510000 | FILTER, DUPLEX, | 3 GTG LUBE FILTER DELTA HIGH | 12 | 6 |
| 3510000 | LOCAL CONTROL PA | LOCOP LIGHT INDICATOR OUT | 3 | 2 |
| 3510000 | LOCAL CONTROL PA | LOCOP LIGHTS OOC | 2 | 1 |
| 3510000 | LOCAL CONTROL PA | LOCOP LIGHTS BULBS OOC | 2 | 2 |
| 3510000 | LOCAL CONTROL PA | LOCOP LIGHT BULBS OOC | 2 | 1 |
| 3510000 | LOCAL CONTROL PA | LOCOP LIGHT OOC | 4 | 1 |
| 3510000 | LOCAL CONTROL PA | LOCOP LIGHT BULBS OOC | 3 | 1 |
| 3510000 | FILTER, DUAL | NR2 GTG F/O FILTERS CLOGGED | 5 | 4 |
| 3510000 | FILTER, LUBE OIL | TECH SUPPORT FOR HI L/O PRESS | 1 | 0 |
| 3510000 | FILTER, DUPLEX, | 3 GTG SYNT L/O FILTERS | 2 | 3 |
| 3510000 | STARTER ASSEMBLY | NR 3 SSGTG STARTER PAD BOLT | 21 | 1 |
| 3510000 | NOZZLE, FUEL ASS | FAILING FUEL NOZZLES #2 GTG | 60 | 6 |
| 3510000 | FILTER FDPRESS L | FUEL FILTER NEED REPLACEMENT | 25 | 6 |
| 3510000 | NOZZLE, FUEL ASS | NR#1 SSGTG F/O NOZZLE CHG OUT | 25 | 1 |
| 3510000 | NOZZLE, FUEL ASS | NR#1 SSGTG F/O NOZZLES CHG OUT | 25 | 1 |
| 3510000 | NOZZLE, FUEL ASS | NR#1 SSGTG F/O NOZZLES GHG OUT | 19 | 2 |
| 3510000 | NOZZLE, FUEL ASS | NR#1 SSGTG F/O NOZZZLE CHG OUT | 25 | 1 |
| 3510000 | NOZZLE, FUEL ASS | NR#1 SSGTG F/O NOZZLES CHG OUT | 25 | 1 |
| 3510000 | NOZZLE, FUEL ASS | NR#1 SSGTG F/O NOZZLE CHG OUT | 25 | 1 |
| 3510000 | VALVE, BLEED AIR | 2 GTG BLEED VLV CONT AIR LEAK | 34 | 0 |
| 3510000 | FILTER FDPRESS L | 2 GTG F/O FILT | 30 | 4 |
| 3510000 | FILTER FDPRESS H | 2 GTG HP FILT ELEMENTS CLOGGED | 20 | 2 |
| 3510000 | FILTER, DUAL | 3 GTG F/O FILT CLOGGED | 20 | 2 |
| 3510000 | FILTER FDPRESS L | 3 GTG F/O FILT CLOGGED | 20 | 1 |
| 3510000 | LOCAL CONTROL PA | NR1 GTG LOCOP RPM METER DEGRAD | 28 | 2 |
| 3510000 | FILTER, DUAL | 2 GTG F/O FILTER CLOGGED | 60 | 2 |
| 3510000 | FILTER, DUAL | NR1 SSGTG F/O FILTER CHG OUT | 4 | 2 |
| 3510000 | FILTER FDPRESS L | NR1 SSGTG F/O FILTER CHG OUT | 4 | 1 |
| 3510000 | NOZZLE, FUEL ASS | FAULTY FUEL NOZZLES 3 GTG | 10 | 1 |
| 3510000 | LOCAL CONTROL PA | 3GTG LOCAL FUEL TEMP CARD FAUL | 610 | 1 |
| 3510000 | SSGTG NO. 3 NO-B | NR3 GTG NBPS REPLACEMENT | 7 | 1 |
| 3510000 | NOZZLE, FUEL ASS | REPLACE FUEL NOZZLES 400 HOURS | 5 | 0 |
| 3510000 | FILTER, DUAL | 2 GTG F/O FILTER CLOGGED | 30 | 6 |
| 3510000 | FILTER FDPRESS L | 2 GTG F/O FILTER CLOGGED | 30 | 6 |
| 3510000 | NOZZLE, FUEL ASS | CLOGGED F/O NOZZLES | 75 | 6 |
| 3510000 | STARTER ASSEMBLY | 2GTG STARTER WEEPS OIL | 25 | 2 |
| 3510000 | VALVE,CONTROL-TE | 2GTG TEMP REG VALVE FAILED | 90 | 1 |
| 3510000 | FILTER, DUPLEX, | 3 GTG L/O FILTER CLOGGED | 10 | 1 |
| 3510000 | FILTER, LUBE OIL | 3 GTG L/O FILTER CLOGGED | 10 | 1 |
| 3510000 | COUPLING, FLEXIB | NR1 SSGTG COUPLING REPLACEMENT | 40 | 1 |
| 3510000 | FILTER, DUPLEX, | NR1 SSGTG L/O FILTERS DIRTY | 6 | 1 |
| 3510000 | STRAINER FLANGED | PLEASE CANCEL | 1 | 0 |
| 3510000 | FILTER, DUPLEX, | REPLACE ENG L/O FILTER | 2 | 2 |
| 3510000 | FILTER, DUPLEX, | 2 GTG CLOGGED L/O FILTERS | 40 | 1 |
| 3510000 | NOZZLE, FUEL ASS | NR 1 SSGTG F/O NOZZLES CHG OUT | 10 | 2 |
| 3510000 | NOZZLE, FUEL ASS | NR1 SSGTG F/O NOZZLES CHG OUT | 10 | 2 |
| 3510000 | NOZZLE, FUEL ASS | NR1 SSGTG F/O NOZZLES CHG OUT | 10 | 2 |
| 3510000 | NOZZLE, FUEL ASS | NR1 SSGTG F/O NOZZLES CHG OUT | 10 | 2 |
| 3510000 | NOZZLE, FUEL ASS | NR1 SSGTG F/O NOZZLES CHG OUT | 10 | 2 |
| 3510000 | NOZZLE, FUEL ASS | NR 1 SSGTG F/O NOZZLES CHG OUT | 10 | 3 |
| 3510000 | FILTER, DUAL | 2 GTG CLOGGED F/O FILTERS | 45 | 9 |
| 3510000 | FILTER FDPRESS L | 2 GTG CLOGGED F/O FILTERS | 50 | 6 |
| 3510000 | FILTER FDPRESS L | REPLACE FUEL FILETER ELEMENT | 6 | 6 |
| 3510000 | FILTER FDPRESS L | REPLACE FUEL FILTER CLOGGED | 6 | 1 |
| 3510000 | FILTER, DUPLEX, | 2GTG CLOGGED L/O FILTERS | 55 | 1 |
| 3511000 | ENGINE ASSY GAS | FAULTY THERMAL COUPLE 1 GTG | 7 | 1 |
| 3511000 | ENGINE ASSY GAS | HOT STARTS NR 2 GTG | 4 | 1 |
| 3511000 | ENGINE ASSY GAS | HOT STARTS NR 2 GTG | 4 | 1 |
| 3511000 | ENGINE ASSY GAS | HOT STARTS NR 2 GTG | 4 | 1 |
| 3511000 | ENGINE ASSY GAS | HOT STARTS NR 2 GTG | 4 | 1 |
| 3511000 | ENGINE ASSY GAS | HOT STARTS NR 2 GTG | 4 | 1 |
| 3511000 | ENGINE ASSY GAS | HOT STARTS NR 2 GTG | 4 | 1 |
| 3511000 | ENGINE ASSY GAS | 2GTG FAULTY TERMINAL BLOCK | 3 | 1 |
| 3511000 | ENGINE ASSY GAS | THERMOCOUPLE TERM FAULTY 1GTG | 3 | 1 |
| 3511000 | ENGINE ASSY GAS | 3GTG THERMOCOUPLE TERM FAULTY | 2 | 1 |
| 3511000 | ENGINE ASSY GAS | DIRTY NOZZLES | 20 | 2 |
| 3511000 | ENGINE ASSY GAS | DIRTY NOZZLE | 20 | 2 |
| 3511000 | ENGINE ASSY GAS | NR 2 GTG THERMOCOUPLE TEMP HOT | 6 | 0 |
| 3511000 | ENGINE ASSY GAS | 1GTG BLEED AIR/SPLIT LINE LEAK | 27 | 8 |
| 3511000 | ENGINE ASSY GAS | B/A LEAKS ON NR 3 SSGTG | 1 | 2 |
| 3511000 | ENGINE ASSY GAS | TURBINE TEMPS HIGH 2 GTG | 333 | 3 |
| 3511000 | ENGINE ASSY GAS | DEAD BUS LOGIC SLOW | 9 | 0 |
| 3511000 | ENGINE ASSY GAS | DEAD BUS LOGIC SLOW 3 GTG | 9 | 0 |
| 3511000 | ENGINE ASSY GAS | THERMOCOUPLE TEMPS HIGH | 101 | 0 |
| 3511000 | ENGINE ASSY GAS | #2 SSGTG MECH MCA | 1 | 0 |
| 3511000 | ENGINE ASSY GAS | #3 SSGTG MECH MCA | 1 | 0 |
| 3511000 | ENGINE ASSY GAS | #1 SSGTG MECH MCA | 1 | 0 |
| 3511000 | ENGINE ASSY GAS | F/O NOZZLES FAILED | 36 | 0 |
| 3511000 | ENGINE ASSY GAS | LIQUID FUEL VLV MOD REQUIRED | 1 | 0 |
| 3511000 | ENGINE ASSY GAS | CDP XDCR FAULTY | 1 | 0 |
| 3511000 | ENGINE ASSY GAS | INSULATION BLANKETS WORN | 24 | 0 |
| 3511000 | ENGINE ASSY GAS | OIL FILTR INLET PRESSURE FAULT | 1 | 0 |
| 3511000 | ENGINE ASSY GAS | FAULTY LUBE OIL PRESSURE READ | 550 | 0 |
| 3511000 | ENGINE ASSY GAS | 3 GTG BEARING REPLACEMENT | 13 | 49 |
| 3511000 | GOVERNOR, ELECTR | 3 GTG EHGA VLV REPLACEMENT | 2 | 0 |
| 3511000 | ENGINE ASSY GAS | #2 GTG PICK UP ASSEMBLY | 9 | 0 |
| 3511000 | ENGINE ASSY GAS | #1 GTG PICK UP ASSEMBLY | 9 | 0 |
| 3511000 | GOVERNOR, ELECTR | NR 3 EHGA REPLACEMENT | 15 | 0 |
| 3511000 | ENGINE ASSY GAS | LIQUID FUEL VLV MOD REQUIRED | 20 | 1 |
| 3511000 | GOVERNOR, ELECTR | EHGA REPLACEMENT | 25 | 1 |
| 3511000 | GOVERNOR, ELECTR | #3 GTG WILL NOT ADJUST FREQ | 210 | 0 |
| 3511000 | ENGINE ASSY GAS | 3GTG OVER TEMP, REPLACE NOZZLE | 10 | 0 |
| 3511000 | ENGINE ASSY GAS | REPLACE 3GTG LIGHTHOUS SEALE | 260 | 14 |
| 3511000 | ENGINE ASSY GAS | BLEED AIR LEAKS NR1 SSGTG | 12 | 1 |
| 3511000 | GENERATOR SET SK | DITRERATED GAGE LINE. | 8 | 1 |
| 3511000 | ENGINE ASSY GAS | 3 GEN SPEED PICK UP | 30 | 1 |
| 3530000 | GAS TURB GEN ENC | MODULE LIGHTS | 1 | 1 |
| 3530000 | GAS TURB GEN ENC | REPLACE MODULE BULBS | 1 | 1 |
| 3530000 | GAS TURB GEN ENC | DETRERATED GAGR LINE. | 8 | 0 |
| 3550000 | GENERATOR A23938 | 2 GTG ZINCS ERODED AWAY | 50 | 1 |
| 3550000 | GENERATOR A23938 | 3 GTG ZINC ANNODES ERODED | 50 | 2 |
| 3561000 | DIFFERENTIAL PRE | REPIAR/REPLACE GUAGE | 2 | 0 |
| 3561000 | GAGE, DIFFERENTI | FAULTY DIFF GAGE/SW GTM2B INTA | 30 | 1 |
| 3561000 | CONTROL PANEL, M | BLOW-IN DOORS LIGHTS OOD | 10 | 3 |
| 3573000 | MOISTURE SEPARAT | NO SCOTT FOAM ON BOARD | 9 | 0 |
| 3573000 | MOISTURE SEPARAT | 1GTG AGGLOMERATORS WORN | 30 | 1 |
| 3573000 | MOISTURE SEPARAT | NR SSGTG AGLOMERATOR FILTERS | 2 | 1 |
| 3574000 | SSGTG NO.1 COOLI | GTG FAN INOP AT LOCOP | 8 | 0 |
| 3574000 | CONTROLLER (SSGT | FAN TRIPS ON OVERLOAD | 5 | 2 |
| 3574000 | CONTROLLER (SSGT | 3 GTG FAN CAN'T STOP AT LOCOP | 25 | 3 |
| 3576000 | DAMPER, AIR COOL | VENT DAMPER FAILED TO CLOSE | 59 | 2 |
| 3576000 | EXCITATION CONTR | NR1 GTG LOSS OF OUTPUT VOLTAGE | 400 | 0 |
| 3602000 | BATTERY CHARGING | OVERHAUL STBD BOAT LCKR CHRGR | 62 | 2 |
| 3705000 | PYWI 64157 | DDG51 CLASS PYWI 64157 REQD | 2 | 24 |

Section 2. 4xxxxxx codes: Electrical Power Distribution Systems  repairs for the year 1999

4xxxxxx Equipment Configuration appearing in 3M repairs for this DDG class ship:

4000000		DISTRIBUTION SYSTEMS, ELECTRICAL POWER

4101000		SWITCHBOARD, SHIPS SERVICE, 60HZ

4103000		SWITCHBOARD, SHIPS SERVICE, 400HZ

410B000	SWITCHBOARD, GROUP CONTROL (CONTROLS ELECTRIC PLANT)

410C000	SWITCHBOARD, LOAD CENTER

410E000	SWITCHBOARDS, INTERIOR COMMUNICATION, MAIN

4301000		PANELS, POWER, CIRCUIT BREAKER

4306000		HOOKUP SYSTEMS, SHORE POWER

4309000		BUS TRANSFER, AUTOMATIC

430B000	CABLING, DISTRIBUTION

4501000		TRANSFORMERS, LIGHTING DISTRIBUTION

4503000		PANELS, LIGHTING DISTRIBUTION

4505000		FIXTURES, LIGHTING, PERMANENT MOUNTED

4506000		FIXTURES, LIGHTING, PORTABLE

4704000		MOTOR-GENERATOR SET, DC TO 400HZ (OUTPUT)

470E000	RECTIFIER, POWER SUPPLY, 60HZ TO DC, CATHODE PROTECT

Longest repair man-hours for single repair for this ship (top 20)

| EIC | equipment_nomenclature | csmp_narrative_summary | man_hours | total_part_issues |
| --- | --- | --- | --- | --- |
| 4000000 | CABLE REPAIR ELE | MER2 POWER PANEL CABLE DAMAGE | 100 | 0 |
| 4309000 | AUTOMATIC BUS TR | 3-254-2 ABT BURNT COMPONENTS | 75 | 3 |
| 4309000 | AUTOMATIC BUS TR | FAULTY GTM2B ABT | 74 | 0 |
| 4501000 | VERT DROP LGHTLI | FIX DROPLINE LHGT RCPT CONDUIT | 41 | 2 |
| 4505000 | FLUORESCENT CEIL | INSUFFICIENT LIGHTING | 30 | 0 |
| 4309000 | AUTOMATIC BUS TR | NR3 F.MAIN ABT WON'T GO ALTERN | 29 | 6 |
| 4101000 | 2SG SHIPS SERVIC | MISSING JUMPERS ON SWBD AGD | 20 | 0 |
| 4101000 | 3SG SHIPS SERVIC | MISSING JUMPERS ON SWBD AGD | 20 | 0 |
| 4506000 | LANTERN, RELAY O | NO EMERGENCY LIGHTING FOR SAM | 16 | 0 |
| 4505000 | INCANDESCENT DEC | DETERIORATING BULBS & GASKETS | 15 | 6 |
| 470E000 | CATHODIC PROTECT | CLEAN/INSPECT CATHODIC ANODES | 14 | 0 |
| 4505000 | FLUORESCENT CEIL | NR3 GTG ROOM LIGHTING BOX | 14 | 5 |
| 4301000 | CABLE ASSY SHORE | MANUF 3 SHORE POWER PIGTAILS | 13 | 0 |
| 4101000 | DIST. PANEL | DAMAGE CIRCUIT BRKR ON PANEL | 13 | 1 |
| 4505000 | LIGHT FIXTURE, C | INADEQUATE LIGHTING | 12 | 3 |
| 4103000 | ACSFC RECTIFIER | FAULTY RECTIFIER MODULE #4 | 10 | 0 |
| 4501000 | CONVENIENCE RECE | RELOCATE RECEPTACLE | 10 | 0 |
| 4505000 | FIXTURE, LIGHT | REPLACE LIGHT FILTERS | 10 | 1 |
| 4103000 | ACSFC INVERTER | BLOWER MOTOR FAILING | 9 | 1 |
| 4103000 | ACSFC INVERTER | FAULTY FAN, CENTRIFUGAL | 9 | 1 |

Full listing of 4xxxxxx repairs for columns EIC, nomenclature, sailor narrative maintenance action summary, ship’s force man-hours and total part issues.

| EIC | equipment_nomenclature | csmp_narrative_summary | man_hours | total_part_issues |
| --- | --- | --- | --- | --- |
| 4000000 | MCT CABLE BLOCKS | MCT CABLING BLOCKS BROKEN | 1 | 0 |
| 4000000 | GCCS-M UPS | FAILED GCCS-M UPS | 1 | 0 |
| 4000000 | CABLE REPAIR ELE | MER2 POWER PANEL CABLE DAMAGE | 100 | 0 |
| 4101000.00 | 3SG SHIPS SERVIC | REPLACE INDICATING LT BULBS | 2 | 1 |
| 4101000 | 1SG SHIPS SERVIC | #1 SWBD BLOWN FUSE | 3 | 1 |
| 4101000 | 3SG SHIPS SERVIC | SWBDS HAVE BURNED LIGHT BULBS | 1 | 2 |
| 4101000 | DIST. PANEL | DAMAGE CIRCUIT BRKR ON PANEL | 13 | 1 |
| 4101000 | 2SG SHIPS SERVIC | SEVERAL BURNED LIGHT BULBS | 3 | 4 |
| 4101000 | 1SG SHIPS SERVIC | SWBD LIGHT INDICATORS ARE OUT | 2 | 2 |
| 4101000 | 1SG SHIPS SERVIC | SWBS LIGHTS OOC | 6 | 2 |
| 4101000 | 1SG SHIPS SERVIC | SWBS LIGHTS OOC | 2 | 2 |
| 4101000 | 1SG SHIPS SERVIC | SWBD LIGHTS OOC | 2 | 2 |
| 4101000 | 1SG SHIPS SERVIC | SWBD LIGHTS OOC | 3 | 2 |
| 4101000 | 1SG SHIPS SERVIC | SWBD LIGHTS OOC | 2 | 3 |
| 4101000 | SWITCH, CUTOUT | FAULTY LIGHT SWITCH | 4 | 2 |
| 4101000 | 2SG SHIPS SERVIC | MISSING JUMPERS ON SWBD AGD | 20 | 0 |
| 4101000 | 3SG SHIPS SERVIC | MISSING JUMPERS ON SWBD AGD | 20 | 0 |
| 4101000 | 1SG SHIPS SERVIC | MISSING JUMPERS ON SWBD AGD | 20 | 0 |
| 4103000 | FAULT LOAD ISOLA | FAULTY FIU #0637/FWD PWR CNVR | 5 | 1 |
| 4103000 | ACSFC RECTIFIER | FAULTY RECTIFIER MODULE FUSE | 1 | 1 |
| 4103000 | ACSFC RECTIFIER | FAULTY RECTIFIER MODULE | 8 | 1 |
| 4103000 | DISTRIBUTION BOX | DIST. BOXES BLOWN FUSES | 1 | 2 |
| 4103000 | FAULT LOAD ISOLA | BAD MODULE OF FIU SN1021 | 7 | 1 |
| 4103000 | ACSFC RECTIFIER | FAULTY RECTIFIER MODULE | 8 | 1 |
| 4103000 | 2SF SHIP'S SERVI | AMPMETER INOPERATIVE | 5 | 0 |
| 4103000 | ACSFC INVERTER | BLOWER MOTOR FAILING | 9 | 1 |
| 4103000 | AIR COOLED STATI | #1 SFC MCA | 1 | 0 |
| 4103000 | AIR COOLED STATI | #2 SFC MCA | 1 | 0 |
| 4103000 | 1SF SHIP'S SERVI | BURNED LIGHTS AT SWBDS | 1 | 0 |
| 4103000 | FAULT LOAD ISOLA | FAULTY FIU S/N 0649 | 7 | 2 |
| 4103000 | ACSFC RECTIFIER | FAULTY RECTIFIER MODULE | 2 | 0 |
| 4103000 | ACSFC INVERTER | FAULTY FAN, CENTRIFUGAL | 9 | 1 |
| 4103000 | ACSFC RECTIFIER | FAULTY RECTIFIER MODULES 1 & 3 | 8 | 2 |
| 4103000 | ACSFC RECTIFIER | FAULTY RECTIFIER MODULE #4 | 10 | 0 |
| 4103000 | FAULT LOAD ISOLA | FAULTY FIU | 3 | 0 |
| 410B000 | DISTRIBUTION BOX | BAD ROTARY SWITCHES | 8 | 0 |
| 410C000 | GROUNDING STRAP | GRND STRAPS DETERIORATED | 7 | 2 |
| 410E000 | MAIN IC SWITCHBO | MAIN IC SWBD, BLOWN INDICATORS | 3 | 1 |
| 4301000 | GROUND DETECTOR | BURNED LIGHTS AT GROUND DETECT | 1 | 0 |
| 4301000 | CABLE ASSY SHORE | MISSING CHAFFING RAIL | 4 | 0 |
| 4301000 | CABLE ASSY SHORE | MANUF 3 SHORE POWER PIGTAILS | 13 | 0 |
| 4306000 | SHORE POWER RECE | BURNED OUT BULBS SHORE POWER | 8 | 1 |
| 4309000 | AUTOMATIC BUS TR | NR3 F.MAIN ABT WON'T GO ALTERN | 29 | 6 |
| 4309000 | AUTOMATIC BUS TR | FAULTY GTM2B ABT | 74 | 0 |
| 4309000 | AUTOMATIC BUS TR | LITYOYFKGFKU | 1 | 0 |
| 4309000 | AUTOMATIC BUS TR | 2BGTM INTERMIT ABT SHIFTING | 50 | 5 |
| 4309000 | DDG AER 66034 | DDG51 CLASS AER 66034 REQD | 2 | 0 |
| 4309000 | AUTOMATIC BUS TR | 3-254-2 ABT BURNT COMPONENTS | 75 | 3 |
| 430B000 | CABLEWAYS | REQ CORRECT CABLEWAY DEFECTS | 1 | 0 |
| 4501000 | INCANDESCENT POR | PORT WEATHERDECK FLOODLT INOP | 3 | 1 |
| 4501000 | STATION MARKING | CORRODED WEATHERDECK RECEPTACL | 5 | 2 |
| 4501000 | LIGHTING SWITCH | DOOR SWITCH BAD | 2 | 0 |
| 4501000 | MOTOR CONTROLLER | VENTILATION SYS S03-143-1 MCA | 1 | 0 |
| 4501000 | CONVENIENCE RECE | RECEPTACLE IS FAULTY | 6 | 0 |
| 4501000 | EMP ASSY | RPLC DETERIORATED EMP ASSY | 1 | 0 |
| 4501000 | VERT DROP LGHTLI | FIX DROPLINE LHGT RCPT CONDUIT | 41 | 2 |
| 4501000 | CONVENIENCE RECE | RELOCATE RECEPTACLE | 10 | 0 |
| 4503000 | LIGHTING DISTRIB | REPLACE BLOWN FUSES | 6 | 6 |
| 4503000 | RECPT WTRTT | REPLACE CORRODED TOPSIDE RECEP | 5 | 0 |
| 4503000 | LIGHTING DISTRIB | SEVERAL BLOWN FUSES | 3 | 6 |
| 4503000 | CONVENIENCE RECE | RECEPTACLE FAULTY | 6 | 4 |
| 4503000 | HEADSET | HEADSET MISSING, NR3 SWBD | 1 | 1 |
| 4505000 | INCANDESCENT DEC | REPLACE INCAND LIGHT BULBS | 2 | 1 |
| 4505000 | FLUORESCENT CEIL | REPLACE BALLASTS AND STARTERS | 6 | 2 |
| 4505000 | LIGHT FIXTURE, C | CHIPPED LIGHT COVER | 4 | 1 |
| 4505000 | FLUORESCENT CEIL | REPLACE STARTERS AND BALLAST | 6 | 3 |
| 4505000 | 2 | REMOVE DESK LAMP FROM CSER 2 | 1 | 0 |
| 4505000 | FLUORESCENT CEIL | LIGHTING FIXTURE | 2 | 1 |
| 4505000 | LIGHT FIXTURES | DIM INCAND LIGHTING FIXTURES | 8 | 1 |
| 4505000 | INCANDESCENT DEC | DIM INCANDESCENT LT FIXTURES | 6 | 2 |
| 4505000 | BOX STATION MARK | REPLACE INCANDESCENT LT BULBS | 3 | 1 |
| 4505000 | FLOURESCENT CEIL | REPLACE DIM VANITY FLOUR LTS | 7 | 2 |
| 4505000 | INCANDESCENT BUL | STBD WEATHERDECK FLOODLTS INOP | 3 | 1 |
| 4505000 | FLUORESCENT CEIL | REPLACE CRACKED LIGHT COVERS | 2 | 1 |
| 4505000 | FLUORESCENT CEIL | REPLACE CRACKED LIGHT COVERS | 2 | 1 |
| 4505000 | FLUORESCENT CEIL | LIGHT WILL NOT LIGHT | 1 | 0 |
| 4505000 | FLUORESCENT CEIL | DIM FLOUR LTS AND BAD STARTERS | 6 | 2 |
| 4505000 | INCANDESCENT DEC | REPLACE BROKEN SEALS | 1 | 1 |
| 4505000 | FLUORESCENT CEIL | INADEQUATE DC DECK LIGHTING | 4 | 0 |
| 4505000 | FLUORESCENT CEIL | REPLACE DEFECTIVE STARTERS | 4 | 2 |
| 4505000 | HAND LANTERN | INSTALL RELAY BATTLE LANTERNS | 2 | 4 |
| 4505000 | FIXTURE, LIGHT | REPLACE LIGHT FILTERS | 10 | 1 |
| 4505000 | FLUORESCENT CEIL | FAULTY BALLAST ON FLRST LIGHT | 2 | 1 |
| 4505000 | LIGHTS | NO RED LIGHTS | 2 | 0 |
| 4505000 | INCANDESCENT DEC | DETERIORATING BULBS & GASKETS | 15 | 6 |
| 4505000 | FLUORESCENT CEIL | REMOVE AND REPLCE LIGHT COVER | 2 | 2 |
| 4505000 | FIXTURE, LIGHT | CRACKED LIGHT COVERS | 5 | 3 |
| 4505000 | FIXTURE, LIGHT | FLOURESCENT BULBS OUT | 6 | 2 |
| 4505000 | FLUORESCENT CEIL | LGHT FIXTURE GROUNDED | 8 | 1 |
| 4505000 | FLUORESCENT CEIL | BROKEN LIGHT COVER | 4 | 1 |
| 4505000 | INCANDESCENT DEC | WEA DECK LIGHTS OUT | 3 | 1 |
| 4505000 | INCANDESCENT CEI | LEAD WIRE SEALS MISSING | 2 | 1 |
| 4505000 | LIGHT FIXTURE, C | INADEQUATE LIGHTING | 12 | 3 |
| 4505000 | FLUORESCENT CEIL | FAULTY RED FILTERS | 6 | 2 |
| 4505000 | FLUORESCENT CEIL | FAULTY FLOUR BULBS AND STARTER | 4 | 2 |
| 4505000 | FLUORESCENT CEIL | BURNT OUT BULBS | 2 | 1 |
| 4505000 | FLUORESCENT CEIL | FAULTY STARTERS IN LIGHT | 2 | 1 |
| 4505000 | FLOURESCENT CEIL | FAULTY STARTERS | 2 | 1 |
| 4505000 | FLUORESCENT CEIL | BURNT OUT FLOURESCENT LIGHTS | 4 | 1 |
| 4505000 | FLUORESCENT CEIL | BAD FLOURESCENT BULBS | 6 | 2 |
| 4505000 | FLUORESCENT CEIL | NR3 GTG ROOM LIGHTING BOX | 14 | 5 |
| 4505000 | INCANDESCENT DEC | FAULTY BULBS AND GASKETS | 7 | 3 |
| 4505000 | FLUORESCENT CEIL | INSUFFICIENT LIGHTING | 30 | 0 |
| 4505000 | FLUORESCENT CEIL | FAULTY LIGHT STARTERS | 4 | 9 |
| 4505000 | FLUORESCENT LIGH | OOC FLOURESCENTS | 10 | 1 |
| 4505000 | WATERLINE SECURI | BURNT OUT FLOODLIGHTS | 6 | 1 |
| 4506000 | LANTERN, RELAY O | NO EMERGENCY LIGHTING FOR SAM | 16 | 0 |
| 4506000 | LANTERN, RELAY O | NO EMERGENCY LIGHTING INSTALL | 6 | 2 |
| 4506000 | RELAY OPERATED L | BLOWN LANTERN BULB | 2 | 2 |
| 4506000 | RELAY OPERATED L | BULB BURNT OUT | 3 | 2 |
| 4506000 | PLOTTING BOARD | PLOTTING BOARD LIGHTS OUT | 4 | 1 |
| 4506000 | CONVENIENCE RECE | WEATHER DECK RECEPTACLES | 1 | 2 |
| 4506000 | RELAY OPERATED L | BATTLE LANTERN BULBS OUT | 3 | 1 |
| 4506000 | CIC STATUS PLOTT | FAULTY ILLUMNATION LAMPS | 4 | 1 |
| 4704000 | SSGTG NO. 1 NO-B | #1 NBPS BURNT CIRCUIT CARDS | 9 | 0 |
| 4704000 | SSGTG NO. 1 NO-B | REPLACE NR1 GTG NBPS | 7 | 1 |
| 4704000 | SSGTG NO. 2 NO-B | NR2 GTG NBPS REPLACEMENT | 7 | 1 |
| 470E000 | CATHODIC PROTECT | CLEAN/INSPECT CATHODIC ANODES | 14 | 0 |

Section 3. 5xxxxxx codes: Missile Systems repairs for the year 1999

Sample listing of the 5xxxxxx EICs for AN/SPY-1appearing in 3M repairs for this ship:

5611310		AS-3851/SPY-1D, ANTENNA

5615600		HD-1140(SERIES)/SPY-1D, COOLER, WATER, ELEC EQUIPMENT

Small sample of 5xxxxxx repairs for columns EIC, nomenclature, sailor narrative maintenance action summary, ship’s force man-hours and total part issues.

| 5611310 | ANTENNA (FWD STB | AN/SPY-1D SPHERE |
| --- | --- | --- |

| 5615600 | AN/SPY-1D & FCS | FAULTY SWITCH AND CONNECTORS |
| --- | --- | --- |
| 5615600 | AN/SPY-1D & FCS | MIXED BED FILTERS HD1140 |
| 5615600 | AN/SPY-1D & FCS | HD1140 MICRON FILTERS |
| 5615600 | AN/SPY-1D & FCS | HEAT EXCHANGER TUBE PLUGS |
| 5615600 | AN/SPY-1D & FCS | DETERIORATED DRIP PAN PRESERVA |
| 5615600 | AN/SPY-1D & FCS | FAULTY PUMP SEALS |
| 5615600 | AN/SPY-1D & FCS | PERIODIC TIME METER READING |
| 5615600 | AN/SPY-1D & FCS | PERIODIC TIME METER READING |
| 5615600 | AN/SPY-1D & FCS | HD-1140 B1/B2 OVERHAUL |
| 5615600 | AN/SPY-1D & FCS | LEAKING HEAT EXCHANGERS |
| 5615600 | AN/SPY-1D & FCS | SKID FILTERS |
| 5615600 | AN/SPY-1D & FCS | FAULTY SEAL |
| 5615600 | AN/SPY-1D & FCS | RELAG COOLING SKID |
| 5615600 | AN/SPY-1D & FCS | FAULTY GUAGE HD-1140 |

Section 4. Dxxxxxx codes: Propulsion system repairs for the year 1999

Dxxxxxx Equipment Configuration appearing in 3M repairs for this DDG class ship:

D110000		TURBINE ASSEMBLY, GAS (LM2500)

D111000		GENERATOR ASSEMBLY, GAS

D113000		TURBINE ASSEMBLY, POWER

D114000		INLET AND EXHAUST COMPONENTS

D130000		ENCLOSURE ASSEMBLY, BASE

D140000		LUBE STORAGE AND CONDITIONING

D310000		GEAR ASSEMBLY, MAIN REDUCTION

D311000		GEAR, MAIN REDUCTION

D410000		PROPELLER ASSEMBLY, REVERSIBLE PITCH, CONTROLLABLE

D411000		HUB/BLADE ASSEMBLY, CRP PROPELLER

D414000		DISTRIBUTION BOX, OIL

D415000		HYDRAULIC SYSTEM

D431300		BEARING ASSEMBLY, STERN TUBE

D500000		AIR SUPPLY GROUP, COMBUSTION

D511000		SEPARATION SYSTEM, MOISTURE

D5401		?

D600000		EXHAUST GROUP

D701000		SERVICE SYSTEM, FUEL OIL

D801000		LUBE OIL SERVICE SYSTEM, MAIN REDUCTION GEAR

D803000		FILL, TRANSFER, PURIFICATION

D901000		PIPING, MAIN SEA WATER

D903000		PUMP ASSEMBLY

DA00000		CONTROL AND SURVEILLANCE SYSTEM, ENGINEERING PLANT

DA11000		CONSOLE, CONTROL

DA30000		CONTROL EQUIPMENT, PROPULSION AND AUXILIARY MACHINERY

DA50000		CONTROL EQUIPMENT, ELECTRIC PLANT

DA51000		CONSOLE, CONTROL

DA60000		CONTROL EQUIPMENT, SHIPS

DA61000		SHIP CONTROL CONSOLE

Longest repair man-hours for single repair for this ship (top 32)

| EIC | equipment_nomenclature | csmp_narrative_summary | man_hours | total_part_issues |
| --- | --- | --- | --- | --- |
| D803000 | LUBE OIL PURIFIE | LOP FAILS TO FLOW FWD | 2225 | 3 |
| D110000 | ASSEMBLY, STARTI | 1A GTRB STARTER DAMAGED | 2015 | 1 |
| D411000 | HUB ASSY, STBD | CRP SUMP LOOSING OIL | 950 | 0 |
| D310000 | CLUTCH, SYNCHRO, | REPLACE 2B SSS CLUTCH | 575 | 0 |
| D500000 | 3 SSGTG AIR INTK | 3 GTG AIR INTAKE CORRODED | 509 | 0 |
| D110000 | VALVE, PRESSURE | GTM 2B SLOW STARTS | 350 | 3 |
| D310000 | CLUTCH, SYNCHRO, | 2B SSS CLUTCH BINDING | 235 | 0 |
| D110000 | CONTROL, FUEL | 2A GTM MFC DAMAGED | 160 | 1 |
| D110000 | CABLE, FEEDBACK | 2A/2B GTM FEEDBACK CABLES BAD | 105 | 2 |
| D111000 | GAS GENERATOR, 2 | 2B GTM SLOW TO ACCELERATE | 110 | 6 |
| D310000 | CLUTCH, SYNCHRO, | NR 2B SSS CLUTCH BINDING | 110 | 0 |
| D410000 | ASSEMBLY, PITCH | STBD PITCH SLOW TO RESPOND | 95 | 1 |
| D433000 | SHAFT HORSEPOWER | STBD SHAFT TORQUE NEEDS CAL | 95 | 0 |
| D433000 | SHAFT HORSEPOWER | STBD TORSIONMETER FAULTY | 79 | 2 |
| D410000 | PUMP, STBY HYDRA | PORT CRP STANDY PMP WEEPS OIL | 70 | 4 |
| D801000 | PUMP, STANDBY LU | 2B LOSP DISCH. PRESS LOW | 70 | 0 |
| D803000 | LUBE OIL PURIFIE | #2 LOP BROKEN BELTS | 70 | 1 |
| D130000 | BASE ENCLOSURE | 2B GTM SLOW TO ACCELERATE | 55 | 3 |
| DA00000 | ELECTRONIC SUPPO | ECM PANEL METER NOT RESET | 55 | 0 |
| D901000 | STRAINER, MASKER | BASKET BEYOND USE | 50 | 1 |
| D130000 | BASE ENCLOSURE | MAIN FUEL CONTROL FAULTY | 49 | 1 |
| D701000 | SOLENOID OPERATE | 2B MODULE FUEL VALVE FAULTY | 48 | 1 |
| D701000 | JP-5 TRANSFER FI | REPLACE SEPARATOR ELEMENTS | 45 | 0 |
| D801000 | PUMP,STANDBY LUB | 1A LOSP WEEPS FROM SEALS | 45 | 0 |
| D903000 | MOTOR, SEAWATER | 5 SWS MOTOR HOT | 45 | 1 |
| D111000 | GAS GENERATOR, 2 | REPLACE FUEL NOZZLES ORINGS | 44 | 6 |
| D903000 | MOTOR, SEAWATER | REPLACE/INSPECT/TEST 5 SWS | 40 | 0 |
| D110000 | ACTUATOR, PLA | 1A PLARA FAULTY | 40 | 1 |
| D410000 | GAGE, DIFFERENTI | MN PUMP DP GAGE OOC | 40 | 1 |
| DA30000 | PROPULSION AUXIL | BELL LOGGER OOC | 38 | 1 |
| D310000 | VALVE, SOLENOID, | 2B PWR TURBINE BRAKE NO ENGAGE | 35 | 2 |
| D110000 | SENSOR, CIT | FAULTY CIT SENSOR | 30 | 1 |

Full listing of Dxxxxxx repairs for columns EIC, nomenclature, sailor narrative maintenance action summary, ship’s force man-hours and total part issues.

| EIC | equipment_nomenclature | csmp_narrative_summary | man_hours | total_part_issues |
| --- | --- | --- | --- | --- |
| D110000 | ASSEMBLY, STARTI | 1A GTRB STARTER DAMAGED | 2015 | 1 |
| D110000 | VALVE, AIR ASSEM | START AIR VALVE FAILED | 12 | 0 |
| D110000 | CPS PREFILTERS | PREFILTERS NED REPLACEING | 16 | 0 |
| D110000 | NOZZLE, FUEL, NO | EXCESSIVE CARBON 2B NOZZLES | 29 | 43 |
| D110000 | CONTROL, FUEL | #2A FTM VSV STOP SCREW NOT TGT | 3 | 0 |
| D110000 | CABLE, MAIN IGNI | WORN IGNITOR CABLE | 12 | 1 |
| D110000 | ACTUATOR, PLA | PLARA INOP | 10 | 0 |
| D110000 | ACTUATOR, PLA | 1A PLARA FAULTY | 40 | 1 |
| D110000 | SENSOR, CIT | FAULTY CIT SENSOR | 30 | 1 |
| D110000 | CONTROL, FUEL | REPLACE 2B MAIN FUEL CONTROL | 1 | 0 |
| D110000 | ACTUATOR, PLA | 2B GG SPEED HIGH FAULTY PLARA | 30 | 1 |
| D110000 | FILTER, DUPLEX | INSPECT AS PER INSERV | 14 | 3 |
| D110000 | FILTER, DUPLEX | CHANGE AS PER INSERV | 14 | 2 |
| D110000 | PUMP, FUEL SERVI | INSPECTION AS PER INSERV | 2 | 7 |
| D110000 | BASE ENCLOSURE | LOCKWIRE NEEDED | 5 | 1 |
| D110000 | VALVE, PRESSURE | GTM 2B SLOW STARTS | 350 | 3 |
| D110000 | ASSEMBLY, STARTI | 2A STARTER DAMAGED | 20 | 0 |
| D110000 | ASSEMBLY, STARTI | 2B/2A GTE STARTER | 45 | 4 |
| D110000 | CABLE, MAIN IGNI | VSV FEEBACK CABLE BINDING | 1 | 0 |
| D110000 | ASSEMBLY, STARTI | 2A GTM FAULTY STARTER | 70 | 2 |
| D110000 | CABLE, FEEDBACK | 2A/2B GTM FEEDBACK CABLES BAD | 105 | 2 |
| D110000 | CONTROL, FUEL | 2A GTM MFC DAMAGED | 160 | 1 |
| D111000 | GAS GENERATOR 1A | DFS DDG58-01-99 | 5 | 0 |
| D111000 | GAS GENERATOR 1B | DFS DDG58-02-99 | 11 | 0 |
| D111000 | GAS GENERATOR 2A | DFS DDG58-03-99 | 13 | 0 |
| D111000 | GAS GENERATOR, 2 | BOLT POSITION INCORRECT | 13 | 0 |
| D111000 | GAS GENERATOR 1B | C SUMP VENT/DRN LEAKS | 7 | 0 |
| D111000 | GAS GENERATOR 1A | 1A/1B/2A GG OVERSPEED | 20 | 0 |
| D111000 | GAS GENERATOR 1A | REPLACED BY JCN EMO10700 | 2 | 0 |
| D111000 | GAS GENERATOR 1A | #1A GTM DAMAGED POWER CABLE | 13 | 0 |
| D111000 | GAS GENERATOR 2A | #2A GTM LOOSE SPEED PICKUP | 2 | 1 |
| D111000 | GAS GENERATOR 2A | #2B GTM LO CHECK VLV LEAKS | 16 | 0 |
| D111000 | GAS GENERATOR, 2 | #2B GTM MCA | 1 | 0 |
| D111000 | GAS GENERATOR 1B | #1B GTM TIGHTEN IGNITION LEADS | 1 | 0 |
| D111000 | GAS GENERATOR 1A | #1A BOKEN WIRE LOOSE RTD WIRE | 1 | 0 |
| D111000 | GAS GENERATOR 1A | #1A GTN LO ACCUM ON STARTER | 13 | 0 |
| D111000 | GAS GENERATOR 1A | #1A LOOSE POWER LEADS | 1 | 0 |
| D111000 | GAS GENERATOR 1B | #1B 28V POWER LEADS LOOSE | 1 | 0 |
| D111000 | GAS GENERATOR 1A | #1A SALT CORRISION ON BARRIER | 13 | 0 |
| D111000 | GAS GENERATOR 1B | #1B EXTERNALLY CLEAN | 26 | 0 |
| D111000 | GAS GENERATOR 1B | #1B LOOSE CLAMP | 1 | 0 |
| D111000 | GAS GENERATOR 2A | #2A FTM REPOSITION CLAMP | 3 | 0 |
| D111000 | GAS GENERATOR 2A | #2A GTM MCA | 1 | 0 |
| D111000 | GAS GENERATOR 1A | #1A GTM MCA | 1 | 0 |
| D111000 | GAS GENERATOR 1B | #1B GTM MCA | 1 | 0 |
| D111000 | GAS GENERATOR, 2 | REPLACE FUEL NOZZLES ORINGS | 44 | 6 |
| D111000 | GAS GENERATOR, 2 | 2B GTM SLOW TO ACCELERATE | 110 | 6 |
| D111000 | GAS GENERATOR 2A | 2A ACCELEROMETER DOES NOT WORK | 10 | 2 |
| D111000 | GAS GENERATOR 1B | 1B GTM ACCELEROMETER DOESN'T W | 6 | 1 |
| D111000 | GAS GENERATOR 1A | 1A GTM ACCELEROMETER DOESN'WOR | 8 | 1 |
| D111000 | GAS GENERATOR 1B | 1B ACCELEROMETER CALIBRATION | 5 | 0 |
| D111000 | GAS GENERATOR, 2 | 2B ACCELEROMETER CALIBRATION | 5 | 0 |
| D111000 | GAS GENERATOR 2A | 2A GTM BROKEN PIPING LP TURBIN | 20 | 1 |
| D113000 | POWER TURBINE 2A | #2A GTM CLAMP IS BROKEN | 6 | 1 |
| D113000 | POWER TURBINE 1A | .020 LOCKWIRE NEEDED | 24 | 1 |
| D113000 | POWER TURBINE 2A | 2A ACCELEROMETER CALIBRATION | 5 | 0 |
| D113000 | POWER TURBINE 1A | 1A ACCELEROMETER CALIBRATION | 5 | 0 |
| D114000 | PYWI 64101 | DDG51 CLASS PYWI 64101 REQD | 2 | 0 |
| D114000 | DDG PYWI 64154 | DDG51 CLASS PYWI 64154 REQD | 2 | 0 |
| D130000 | BASE ENCLOSURE | REPLACEMENT OF GASKETS | 12 | 0 |
| D130000 | BASE ENCLOSURE | MAIN FUEL CONTROL FAULTY | 49 | 1 |
| D130000 | BASE ENCLOSURE | 2B GTM SLOW START/ACCELERATION | 15 | 0 |
| D130000 | BASE ENCLOSURE | 2B GTM SLOW TO ACCELERATE | 55 | 3 |
| D140000 | LUBE STORAGE & C | GTM1B L/O FILTER DP FAULTY | 3 | 0 |
| D140000 | LUBE STORAGE & C | 23699 REQD FOR GTE'S | 15 | 1 |
| D140000 | LUBE STORAGE & C | 23699 LOW INVENTORY | 13 | 0 |
| D140000 | LUBE STORAGE & C | 23699 INVENTORY LOW | 2 | 0 |
| D310000 | MAIN REDUCTION G | MRG SUMP CLEANING REQUIRED | 26 | 1 |
| D310000 | PUMP,ATTACHED,MA | #1 ALOP MCA | 1 | 0 |
| D310000 | PUMP,ATTACHED,RE | #2 ALOP MCA | 1 | 0 |
| D310000 | CLUTCH, SYNCHRO, | NR 2B SSS CLUTCH BINDING | 110 | 0 |
| D310000 | VALVE, SOLENOID, | 2B PWR TURBINE BRAKE NO ENGAGE | 35 | 2 |
| D310000 | CLUTCH, SYNCHRO, | 2B SSS CLUTCH BINDING | 235 | 0 |
| D310000 | CLUTCH, SYNCHRO, | REPLACE 2B SSS CLUTCH | 575 | 0 |
| D311000 | DEHUMIDIFIER, DS | STBD HUMIDIFIER FAULTY MOTOR | 11 | 11 |
| D311000 | DEHUMIDIFIER, RE | LIGHT BULB INDICAT. BURNED | 2 | 2 |
| D311000 | DEHUMIDIFIER, RE | NR2 DEHUMIDIFIER CRACK WELDS | 16 | 1 |
| D311000 | DEHUMIDIFIER, RE | BLOWN FUSE | 1 | 1 |
| D410000 | ASSEMBLY, PRAIRI | PRAIRIE AIR SEAL FAILED | 4 | 1 |
| D410000 | FILTER, QUADRUPL | ATTACH CRP FILTERS DIRTY | 2 | 1 |
| D410000 | FILTER, MAIN PUM | CRP QUAD FILTERS DIRTY | 2 | 2 |
| D410000 | PUMP, STBY HYDRA | CRP PUMP WEEPS OIL | 25 | 0 |
| D410000 | VALVE, RELIEF | ADJUSTED OD BOX | 4 | 0 |
| D410000 | VALVE, RELIEF | ADJUSTED OD BOX | 4 | 0 |
| D410000 | ASSEMBLY, PITCH | STBD PITCH SLOW TO RESPOND | 95 | 1 |
| D410000 | STRAINER, MAIN P | FILTERS ARE DIRTY | 6 | 0 |
| D410000 | FILTER, QUADRUPL | FILTERS CLOGGED | 20 | 3 |
| D410000 | FILTER, QUADRUPL | PLEASE DELETE | 20 | 0 |
| D410000 | PUMP, STBY HYDRA | PORT CRP STANDY PMP WEEPS OIL | 70 | 4 |
| D410000 | GAGE, DIFFERENTI | MN PUMP DP GAGE OOC | 40 | 1 |
| D410000 | FILTER, MAIN PUM | QUAD FILTER NEED CHANGED | 10 | 3 |
| D410000 | FILTER, QUADRUPL | REPLACE QUAD FILTES ATTACH CRP | 10 | 4 |
| D410000 | FILTER, AUXILIAR | DUPLEX FILTER CRP REPLACEMENT | 10 | 2 |
| D410000 | FILTER, QUADRUPL | REPLACE CRP QUAD FILTERS | 20 | 4 |
| D410000 | FILTER, MAIN PUM | REPLACE CRP QUAD FILTERS | 20 | 4 |
| D411000 | HUB ASSY, STBD | CRP SUMP LOOSING OIL | 950 | 0 |
| D414000 | DISTRIBUTION BOX | STBD CRP FAILS TO RESPOND | 12 | 3 |
| D414000 | DISTRIBUTION BOX | PMS CHK 2451/A-4R | 4 | 1 |
| D415000 | ASSEMBLY, HOPM | NR1 ELEC CRP PMP CYCLES INCORR | 16 | 0 |
| D415000 | CONTROLLER (LUBE | CRP SUMP HEATER FAILED OPERATE | 30 | 1 |
| D431300 | SHAFT BRNGS | SHAFT BEARING CLNCS REQD | 28 | 0 |
| D431300 | SHAFT BRNG | FTSC TECH ASSIST REQD | 2 | 0 |
| D431300 | SHAFT BRNGS | EVAL MAIN SHAFT BEARING CLNCS | 2 | 0 |
| D431300 | SHAFT BRNG | VIDEO STAVE BEARING PROFILES | 2 | 0 |
| D433000 | STERN TUBE SEAL | MPS PORT MCA | 1 | 0 |
| D433000 | SHAFT HORSEPOWER | STBD TORSIONMETER FAULTY | 79 | 2 |
| D433000 | AFT LINE SHAFT B | RTD'S DEGRADED | 27 | 0 |
| D433000 | SHAFT HORSEPOWER | STBD SHAFT TORQUE NEEDS CAL | 95 | 0 |
| D433000 | FORWARD LINE SHA | 1A LSB OIL SEAL LEAKY | 4 | 1 |
| D500000 | 2B GTM AIR INTKL | CLN AND PRESV. 2B INTK DECKS | 20 | 0 |
| D500000 | 3 SSGTG AIR INTK | 3 GTG AIR INTAKE CORRODED | 509 | 0 |
| D511000 | MOISTURE SEPARAT | 1B GTM FILTER AGGLOMERATORS | 30 | 1 |
| D511000 | MOISTURE SEPARAT | 1A GTM AGGLOMERATORS WORN | 30 | 1 |
| D511000 | MOISTURE SEPARAT | NR 3 SSGTG AGLOMERATOR FILTERS | 21 | 2 |
| D511000 | MOISTURE SEPARAT | 2A INTAKE FILTERS RPLMT | 11 | 3 |
| D511000 | MOISTURE SEPARAT | 2B GTM AGLOMERATOR FILTERS | 1 | 0 |
| D511000 | MOISTURE SEPARAT | 2A GTM AGLOMERATOR FTLR REPLMT | 21 | 1 |
| D5401 | MASKER AIR PIPE | MASKER BELT DRAIN HOSE LEAKS | 22 | 0 |
| D600000 | 3 SSGTG BLISS RM | 3 GTG BLISS RM DECK CORRODED | 9 | 0 |
| D701000 | FUEL SERVICE PRE | FILTER ELEMENT CHANGE REQD | 3 | 2 |
| D701000 | FUEL SERVICE PRE | 1A PREFILTER CLOGGED | 13 | 6 |
| D701000 | FUEL SERVICE PRE | PREFILTERS FOR 2B PREFILTER | 1 | 2 |
| D701000 | FUEL SERVICE PRE | 1B PREFILT HIGH DELTA P | 13 | 6 |
| D701000 | FUEL SERVICE PRE | PREFILTERS FOR 2A PREFILTER | 1 | 2 |
| D701000 | FUEL SERVICE FIL | 1B FILT/SEP WEEP SIGHT GLASS | 11 | 0 |
| D701000 | IND SGT LIQ | 1B FILT/SEP SIGHT GLASS WEEPS | 11 | 3 |
| D701000 | FUEL SERVICE PRE | REPLACEMENT 2A PERFILTER | 4 | 2 |
| D701000 | FUEL SERVICE PRE | DIRTY FILTERS | 2 | 2 |
| D701000 | FUEL SERVICE PRE | FILTERS DIRTY | 2 | 2 |
| D701000 | FUEL SERVICE PRE | 2B F/O COALSER FILTER | 1 | 0 |
| D701000 | FUEL SERVICE FIL | FILTERS ARE DIRTY | 2 | 1 |
| D701000 | FUEL SERVICE FIL | FILTERS ARE DIRTY | 2 | 1 |
| D701000 | FUEL SERVICE FIL | DP HIGH REPLACE COALESCER | 13 | 1 |
| D701000 | FUEL SERVICE PUM | #2A FO SERVICE PUMP MCA | 1 | 0 |
| D701000 | FUEL SERVICE PUM | #2B FO SERVICE PUMP MCA | 1 | 0 |
| D701000 | FUEL SERVICE PUM | #1B FO SERVICE PUMP MCA | 1 | 0 |
| D701000 | FUEL SERVICE PUM | #1A FO SERVICE PUMP MCA | 1 | 0 |
| D701000 | FILL & SPLY VLV | ROG 2-FS-V-41 MCA | 1 | 0 |
| D701000 | FUEL SPLY TO GEN | ROG GFS3-V-6A | 1 | 0 |
| D701000 | FUEL RETURN ELEC | ROG 2FS-V-48B | 1 | 0 |
| D701000 | SSGTG #2SPCY | ROG GFS2-V-1 MCA | 1 | 0 |
| D701000 | MO BHD CO | ROG MD-V-45 MCA | 1 | 0 |
| D701000 | MO BLG SUCT COV | ROG MD-V-3 MCA | 1 | 0 |
| D701000 | QUICK CLOSING GA | ROG 1-FS-V-1B MCA | 1 | 0 |
| D701000 | QUICK CLOSING GA | ROG 1-FS-V-1A MCA | 1 | 0 |
| D701000 | QUICK CLOSING GA | ROG 2-FS-V-1A MCA | 1 | 0 |
| D701000 | QUICK CLOSING GA | ROG 2-FS-V-1B MCA | 1 | 0 |
| D701000 | FILL & SUPPLY | ROG 1-FS-V-41 MCA | 1 | 0 |
| D701000 | THRUST BRG DRN | ROG OW-V-217 MCA | 1 | 0 |
| D701000 | SW CLG MN BHD CO | ROG SW-V-6 MCA | 1 | 0 |
| D701000 | RFR CND SPLY COV | ROG SW-V-411 | 1 | 0 |
| D701000 | INDICATOR, DIFFE | 1A FIL/SEP DP GAGE FAILED | 22 | 1 |
| D701000 | FUEL SERVICE PRE | 1A PREFILTER GAGE WILL NOT CAL | 12 | 0 |
| D701000 | INDICATOR, DIFFE | PREFILTER GAGE FAILED CAL | 24 | 1 |
| D701000 | INDICATOR, DIFFE | 1B FILT/SEP GAGE FAILED | 22 | 1 |
| D701000 | ASSEMBLY, CONTRO | MORPAC FUSE HOLDER BROKEN | 4 | 1 |
| D701000 | FUEL SERVICE PRE | 1A PREFILTER GAGE FAILED | 2 | 0 |
| D701000 | FUEL SERVICE PRE | 1B PPREFILTER DP GAGE FAILED | 3 | 1 |
| D701000 | FUEL SERVICE PRE | 2A PRE-FILTERS DELTA P HIGH | 4 | 2 |
| D701000 | FUEL SERVICE PRE | REPLACE FUEL ELEMENT | 6 | 2 |
| D701000 | FUEL SERVICE PRE | REPLACE PRE-FILTER ELEMENT | 14 | 2 |
| D701000 | FUEL SERVICE FIL | 2B FILT/SEP DP HIGH | 30 | 2 |
| D701000 | FUEL SERVICE FIL | 2A FILTER SEP DELTA P HIGH | 20 | 2 |
| D701000 | FUEL SERVICE PRE | 2B PRE FILT CLOGGED | 20 | 2 |
| D701000 | FUEL SERVICE FIL | COALSER FILTER CHG OUT | 6 | 3 |
| D701000 | INLET CUTOUT VAL | 1A CLSER FLTR INLT VLV REPAIR | 14 | 1 |
| D701000 | FUEL SERVICE FIL | 1A COALSER SUP GAGE REPLACEMT | 12 | 2 |
| D701000 | FUEL SERVICE PRE | PREFILTER NEEDS REPLACEMENT | 12 | 2 |
| D701000 | FUEL SERVICE FIL | CAOLESCER ELEM. NEEDS REPLACEM | 14 | 2 |
| D701000 | JP-5 TRANSFER FI | REPLACE SEPARATOR ELEMENTS | 45 | 0 |
| D701000 | FUEL SERVICE PRE | REPLACE PRE-FILETER ELE. DP HI | 5 | 2 |
| D701000 | FUEL SERVICE FIL | PLEASE DELETE WRONG APL | 1 | 0 |
| D701000 | SOLENOID OPERATE | 2B MODULE FUEL VALVE FAULTY | 48 | 1 |
| D801000 | VALVE,RELIEF,DIS | RLF VLV HYDRO TESTING REQUIRED | 1 | 0 |
| D801000 | VALVE,RELIEF,DIS | RLF VLV HYDRO TESTING REQUIRED | 1 | 0 |
| D801000 | VALVE,RELIEF,DIS | RLF VLV HYDRO TESTING REQUIRED | 1 | 0 |
| D801000 | VALVE,RELIEF,DIS | RLF VLV HRYDR TEST REQUIRED | 15 | 0 |
| D801000 | VALVE,RELIEF,DIS | RLF VLV HYDRO TEST REQUIRED | 15 | 0 |
| D801000 | VALVE,RELIEF,DIS | RLF VLV HYDRO TEST REQUIRED | 10 | 0 |
| D801000 | VALVE,RELIEF,DIS | PT ATTCH LOSP REQ HYDO TESTED | 5 | 0 |
| D801000 | VALVE,RELIEF,DIS | 1A LOSP RELIEF VLV REQ HYDRO | 4 | 0 |
| D801000 | VALVE,RELIEF,DIS | 2B LOSP RELIEF REQ HYDRO TEST | 6 | 0 |
| D801000 | STRAINER,REDUCTI | NR1MRG LO FILTER FAILURE | 27 | 2 |
| D801000 | ELECTROSTATIC PR | PRECIPITATOR LIGHT BURNED OUT | 2 | 1 |
| D801000 | PUMP,STANDBY LUB | 2A LOSP MECH SEAL FITTING LEAK | 21 | 0 |
| D801000 | PUMP, STANDBY LU | 2B LOSP MECH SEAL LEAK FITTING | 21 | 0 |
| D801000 | COOLER,REDUCTION | COOLER IS DIRTY | 2 | 0 |
| D801000 | PUMP,STANDBY LUB | 1A LOSP WEEPS FROM SEALS | 45 | 0 |
| D801000 | PUMP,STANDBY LUB | 1B LOSP WEEPS FROM SEALS | 45 | 0 |
| D801000 | VALVE,CHECK,SUCT | 1A LOSP SUCT CK VLV FAILED | 32 | 0 |
| D801000 | PUMP,STANDBY LUB | #1A SLOP MCA | 1 | 0 |
| D801000 | PUMP,STANDBY LUB | #1B SLOP MCA | 1 | 0 |
| D801000 | PUMP,STANDBY LUB | #2A SLOP MCA | 1 | 0 |
| D801000 | PUMP, STANDBY LU | #2B SLOP MCA | 1 | 0 |
| D801000 | STRAINER,REDUCTI | MN L/O STRNER BROKEN O-RING | 2 | 1 |
| D801000 | PUMP, STANDBY LU | 2B LOSP DISCH. PRESS LOW | 70 | 0 |
| D801000 | VALVE,CHECK,DISC | 1A LOSP CHK VLV LEAKAGE | 42 | 0 |
| D803000 | RELIEF VALVE | NR L/O PURIFIER RLF HYDRO TEST | 5 | 0 |
| D803000 | RELIEF VALVE | RLF VLV REQUIRED HYDRO TEST | 11 | 0 |
| D803000 | LUBE OIL PURIFIE | FLOW SWITCH NR 2 L/O PURIFIER | 1 | 1 |
| D803000 | LUBE OIL PURIFIE | THERMOMETER NEEDS CALIBRATION | 4 | 0 |
| D803000 | LUBE OIL PURIFIE | L.O. PURF #2 DISCH PRES GAGE | 4 | 0 |
| D803000 | LUBE OIL PURIFIE | #1 LO PURIFIER MCA | 1 | 0 |
| D803000 | LUBE OIL PURIFIE | #2 LO PURIFIER MCA | 1 | 0 |
| D803000 | CONTROLLER (LUBE | NR2 LOP FLOW SWITCH INOP | 5 | 0 |
| D803000 | LUBE OIL PURIFIE | NR 2 PURIFIER DIRTY | 1 | 0 |
| D803000 | LUBE OIL PURIFIE | NR1 L/O PURIFIER DIRTY | 6 | 4 |
| D803000 | LUBE OIL PURIFIE | PURIFIER CLEANING REQUIRED | 12 | 8 |
| D803000 | LUBE OIL PURIFIE | NR LOP FLOW SWITCH INOP | 5 | 1 |
| D803000 | LUBE OIL PURIFIE | LOP FAILS TO FLOW FWD | 2225 | 3 |
| D803000 | LUBE OIL PURIFIE | NEW L/O PURIFIER DISCH HOSE | 11 | 0 |
| D803000 | LUBE OIL PURIFIE | #2 LOP BROKEN BELTS | 70 | 1 |
| D803000 | LUBE OIL PURIFIE | NEW BELTS FOR NR1 LOP | 12 | 2 |
| D901000 | VALVE,RELIEF,SHO | RLF VLV TESTING REQUIRED | 5 | 0 |
| D901000 | VALVE,DISCHARGE | 8" SWINGCHECK VLV LEAKS BY | 4 | 0 |
| D901000 | VALVE,CHECK,DISC | 8" SWINGCHECK VLV LEAKS BY | 3 | 1 |
| D901000 | STRAINER,A/C CON | BRITTLE ORING/CRACKED BASKET | 3 | 3 |
| D901000 | STRAINER,A/C PLA | BRITTLE O-RINGS A/C STRAINERS | 4 | 1 |
| D901000 | STRAINER,A/C PLA | BRITTLE O-RINGS A/C STRAINERS | 2 | 1 |
| D901000 | VALVE,CUTOUT,REC | SW-V-31 STEM CRACKED | 2 | 1 |
| D901000 | OPERATOR,REMOTE | SW-V-215 ROG U-JOINT BROKEN | 3 | 2 |
| D901000 | SEA VALVE,SW CLG | SW-V-360 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,PORT S | SW-V-512 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,STBD S | SW-V-511 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,PORT S | SW-V-503 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,PORT S | SW-V-502 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,NO4 AC | SW-V-518 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,STBD S | SW-V-500 SV MCA | 1 | 0 |
| D901000 | VALVE,CUTOUT, EM | SW-V-499 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,STBD S | SW-V-491 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,STBD S | SW-V-490 SV MCA | 1 | 0 |
| D901000 | SEA VALVE #1 SW | SW-V-4 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,OVBD D | SW-V-15 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,SW CLG | SW-V-418 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,SEACHE | SW-V-94 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,NO5 SW | SW-V-89 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,NO5 SW | SW-V-92 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,NO5 SW | SW-V-103 SV MCA | 1 | 0 |
| D901000 | SEA VALVE,SEA CH | SW-V-1 SV MCA | 1 | 0 |
| D901000 | VALVE,CUTOUT,OVE | SW-V-226 SV MCA | 1 | 0 |
| D901000 | S/A DDG51-271.04 | SHIPALT DDG51-0271.04D REQD | 1 | 0 |
| D901000 | STRAINER, MASKER | BASKET BEYOND USE | 50 | 1 |
| D901000 | STRAINER, LP AIR | 2 LPAC STRAINER SHIFT LVR BRK | 40 | 3 |
| D901000 | STRAINER, LP AIR | 3 LPAC STRAINER NEEDS REPAIR | 40 | 2 |
| D901000 | STRAINER, MASKER | SW STRAINER NEEDS NEW LAGGING | 3 | 0 |
| D903000 | CONTROLLER,S/W P | LOOSE DIRTY CONNECTION | 4 | 0 |
| D903000 | PUMP, SEAWATER C | #4 MAIN CIRC SW PUMP MCA | 1 | 0 |
| D903000 | PUMP, SEAWATER C | #1 MAIN CIRC SW PUMP MCA | 1 | 0 |
| D903000 | PUMP,SEAWATER CO | #3 MAIN CIRC SW PUMP MCA | 1 | 0 |
| D903000 | PUMP,SEAWATER CO | #5 MAIN CIRC SW PUMP MCA | 1 | 0 |
| D903000 | PUMP, SEAWATER C | #2 MAIN CIRC SW PUMP MCA | 1 | 0 |
| D903000 | PUMP UNIT, SEAWA | BRAZE NR 4 CLG PMP SEAL LINE | 3 | 0 |
| D903000 | MOTOR, SEAWATER | 5 SWS MOTOR HOT | 45 | 1 |
| D903000 | MOTOR, SEAWATER | REPLACE/INSPECT/TEST 5 SWS | 40 | 0 |
| DA00000 | ELECTRONIC SUPPO | VACUUM CLEANER OOC | 2 | 0 |
| DA00000 | ELECTRONIC SUPPO | ECM PANEL METER NOT RESET | 55 | 0 |
| DA00000 | ENGINE CONTROL M | A3/A4 POWER SUPPLIES FUSES | 2 | 2 |
| DA00000 | ELECTRONIC SUPPO | 2A GTM STARTER FAILURE ALARM | 18 | 0 |
| DA00000 | ELECTRONIC SUPPO | REPLACE 1B ESM/IIEC BATTERIES | 5 | 1 |
| DA00000 | ELECTRONIC SUPPO | REPLACE 2B ESM/IIEC BATTERY | 5 | 1 |
| DA00000 | ELECTRONIC SUPPO | REPLACE 1A ESM/IIEC BATTERIES | 5 | 1 |
| DA00000 | ELECTRONIC SUPPO | REPLACE 2A ESM/IIEC BATTERY | 5 | 1 |
| DA00000 | ENGINE CONTROL M | CONTACT LEAD NEEDED | 10 | 1 |
| DA00000 | ELECTRONIC SUPPO | IECC FUSES 250V 1/4 AMP | 2 | 5 |
| DA11000 | EOOW LOGGING UNI | EOOW CONSOLE AIR FILT. DAMAGED | 1 | 0 |
| DA11000 | ASSEMBLY, BELL L | BELL LOGGER PRINTER NEEDS PAPE | 2 | 0 |
| DA11000 | EOOW LOGGING UNI | ROLL OF THERMAL PAPER | 1 | 0 |
| DA11000 | EOOW LOGGING UNI | MCSS CONT CONSOLE MCA | 1 | 0 |
| DA11000 | ASSEMBLY, BELL L | BELL LOGGER LIGHTS OOC | 3 | 1 |
| DA30000 | PROPULSION AUXIL | PORT PITCH ALARM INTERMITTANT | 16 | 0 |
| DA30000 | ASSEMBLY, CHASSI | USH-26 WORN FILTER | 2 | 1 |
| DA30000 | ASSEMBLY, POWER, | FAULTY PACC PWR SUPPLY | 30 | 1 |
| DA30000 | PROPULSION AUXIL | PACC FAULTY PWR SUPPLY | 1 | 0 |
| DA30000 | PROPULSION AUXIL | BELL LOGGER OOC | 38 | 1 |
| DA50000 | ASSEMBLY, LOGIC | EPCC JEL SEM FAULTY | 1 | 0 |
| DA51000 | ELECTRIC PLANT C | 2SG AND 1S-2S BTB CLOSURE PROB | 22 | 0 |
| DA51000 | ELECTRIC PLANT C | EPCC MCA | 1 | 0 |
| DA51000 | ELECTRIC PLANT C | DETERIORATED KEYBOARD | 13 | 1 |
| DA60000 | ASSEMBLY, LOGIC | SCU-1 JEL CARD FAULTY | 3 | 0 |
| DA60000 | SHAFT CONTROL UN | #2 SCU MISSING LED INDICATOR | 3 | 1 |
| DA60000 | ASSEMBLY, LOGIC | SEM, ELECTRONIC FAULTY | 1 | 1 |
| DA60000 | BUBBLE MEMORY | GROUND ON BUBBLE MEMORY | 17 | 1 |
| DA60000 | ASSEMBLY, LOGIC | PITCH CONT SEM FAULTY | 11 | 1 |
| DA60000 | SHAFT CONTROL UN | F/O HI-LOW INDICATOR LOST | 4 | 5 |
| DA60000 | ASSEMBLY, LOGIC | SCU-1 JEL CARD FAULTY | 11 | 1 |
| DA60000 | REPAIR STATION C | PLASMA DISPLAY IS DEFECTIVE | 5 | 0 |
| DA60000 | SHAFT CONTROL UN | SCU #1 MCA | 1 | 0 |
| DA60000 | SHAFT CONTROL UN | #2 SCU MCA | 1 | 0 |
| DA60000 | REPAIR STATION C | RSC MCA | 1 | 0 |
| DA60000 | SHAFT CONTROL UN | 2B GTM HALON RLSE LIGHT ON | 25 | 0 |
| DA61000 | CIRCUIT VS SHIPS | REPLACE GRND DETEC INDIC BULBS | 2 | 2 |
| DA61000 | CIRCUIT VS SHIPS | REPLACE GROUND DETECT BULBS | 6 | 2 |
| DA61000 | CIRCUIT VS SHIPS | GRND DETECT LIGHT BULBS BLOWN | 1 | 1 |
| DA61000 | CIRCUIT VS SHIPS | SCC COURSE INDICATOR FAULTY | 25 | 0 |